## flow rate
pump sizing
fixtures |  | WSFU | number of fixtures | total
private
| water closet - flush tank | 2.2 | 10 | 22
| water closet - flush valve | 6 |  | 0
public
| water closet - flush tank | 5 | 6 | 30
| water closet - flush valve | 10 | 15 | 150
| urinal - 3/4" | 5 | 5 | 25
| urinal - 1" | 10 |  | 0
|  |  | grand total | 227 | WSFU
| equating WSFU to flow rate depends on the type of dominant toilet type, refer to the IPC chart for values | [7 empty] | should the difference is only two fixtures between tank and flush valve, we need to use the flush valve
|  | using the chart for predominantly flush valve, total wsfu equates to |  |  |  | 95.5 | gpm | this is the value that will pulled by looking up 225 WSFU in the table for estimating demand
Irrigation
client supplied input
|  | total irrigation flowrate |  |  |  |  | gpm |  |  | user should only be able to fill up only one of these options
or
| number of sprinkler | flow rate, gpm | duration, minutes
| 10 | 0.75 | 10 |  |  | 75 | gpm
total pump flow rate requirement
simplex (100% capacity) | [5 empty] | 170.5 | gpm
duplex (70% capacity | [5 empty] | 119.35 | gpm
triplex (35% capacity) | [5 empty] | 59.675 | gpm
tdh to be calculated on the next step

## day tank
[6 empty] | 40 | psi
|  |  | total pipe run | [5 empty] | toilet
160
irrigation
elevation from booster pump CL
[7 empty] | 100 | ft
|  | 10 | ft (suction head)
day tank |  |  | booster
total pipe run
20
user supplied
| Discharge side | [8 empty] | rule of thumb
|  | last fixture, pressure requirement |  |  |  | 40 | psi | 92.4 | feet
|  | last fixture, height from pump | [5 empty] | 100 | feet
|  |  | total pipe run |  | 160 | ft
|  |  | loss per 100 feet |  | 1.5 | ft
|  | losses on overall pipe runs | [5 empty] | 2.4 | feet
|  | losses on valves |  |  |  | 5 | psi | 11.55 | feet
|  | losses on fittings (assume 10% of pipe run) | [5 empty] | 16 | feet
[5 empty] | discharge side |  |  | 222.35 | feet
Suction side
|  | head at the suction side | [5 empty] | -10 | feet
|  |  | total pipe run |  | 20 |  |  |  | feet
|  |  | loss per 100 feet |  | 1.5 |  |  |  | feet
|  | losses on overall pipe runs | [5 empty] | 0.3 | feet
|  | losses on valves |  |  |  | 5 | psi | 11.55 | feet
|  | losses on fittings (assume 10% of pipe run) | [5 empty] | 2 | feet
[5 empty] | suction side |  |  | 3.85
|  |  |  | Total head of booster pump |  |  |  | 226.2 | feet
Note on F42: Dexter Mabalot: this is an assumption, rule of thumb
Note on F52: Dexter Mabalot: this is an assumption, rule of thumb

## Municipal line
[6 empty] | 40 | psi
toilet
total pipe run
|  |  |  | 160 |  |  |  |  | irrigation
elevation from booster pump CL
[7 empty] | 100 | ft
|  | 40 | psi
municipal line |  |  | booster
total pipe run
| 75 | [8 empty] | user supplied
rule of thumb
Discharge side
| last fixture, pressure requirement |  |  |  | 40 | psi | 92.4 | feet
| last fixture, height from pump |  |  |  | 100 |  | 100 | feet
|  | total pipe run |  | 160 | ft
|  | loss per 100 feet |  | 1.5 | ft
| losses on overall pipe runs | [5 empty] | 2.4 | feet
| losses on valves |  |  |  | 5 | psi | 11.55 | feet
| losses on fittings (assume 10% of pipe run) | [5 empty] | 16 | feet
|  |  |  | discharge side |  |  | 222.35 | feet
Suction side
| municipal line pressure |  |  |  | 40 | psi | -92.4 | feet
|  | total pipe run |  | 75 |  |  |  | feet
|  | loss per 100 feet |  | 1.5 |  |  |  | feet
| losses on overall pipe runs | [5 empty] | 1.125 | feet
| losses on valves |  |  |  | 5 | psi | 11.55 | feet
| losses on fittings (assume 10% of pipe run) | [5 empty] | 7.5 | feet
|  |  |  | suction side |  |  | -72.225
|  |  | Total head of booster pump |  |  |  | 150.125 | feet
Note on E42: Dexter Mabalot: this is an assumption, rule of thumb
Note on E52: Dexter Mabalot: this is an assumption, rule of thumb