## Table 1
V 2018 'IIRm-g Code (IPC) G1D APPEN IPING SYSTEM | [6 empty] | 1 Upgrade to Premium Fifth Version: Nov 2021
|  | FIXTURE |  |  |  | OCCUPANCY |  |  |  | TYPE OF SUPPLY CONTROL |  |  |  | LOAD VALUES, IN WATER SUPPLY FIXTURE UNITS (wsfu)
[14 empty] | Cold |  |  |  | Hot |  |  |  | Total
|  | Bathroom group |  |  |  | Private |  |  |  | Flush tank |  |  |  | 2.7 |  |  |  | 1.5 |  |  |  | 3.6
|  | Bathroom group |  |  |  | Private |  |  |  | Flushometer valve |  |  |  | 6 |  |  |  | 3 |  |  |  | 8
|  | Bathtub |  |  |  | Private |  |  |  | Faucet |  |  |  | 1 |  |  |  | 1 |  |  |  | 1.4
|  | Bathtub |  |  |  | Public |  |  |  | Faucet |  |  |  | 3 |  |  |  | 3 |  |  |  | 4
|  | Bidet |  |  |  | Private |  |  |  | Faucet |  |  |  | 1.5 |  |  |  | 1.5 |  |  |  | 2
|  | Combination fixture |  |  |  | Private |  |  |  | Faucet |  |  |  | 2.25 |  |  |  | 2.25 |  |  |  | 3
|  | Dishwashing machine |  |  |  | Private |  |  |  | Automatic |  |  |  | - |  |  |  | 1.4 |  |  |  | 1.4
|  | Drinking fountain |  |  |  | Offices, etc. |  |  |  | 318" valve |  |  |  | 0.25 |  |  |  | - |  |  |  | 0.25
|  | Kitchen sink |  |  |  | Private |  |  |  | Faucet |  |  |  | 1 |  |  |  | 1 |  |  |  | 1.4
|  | Kitchen sink |  |  |  | Hotel, restaurant |  |  |  | Faucet |  |  |  | 3 |  |  |  | 3 |  |  |  | 4
|  | Laundry trays (1 to 3) |  |  |  | Private |  |  |  | Faucet |  |  |  | 1 |  |  |  | 1 |  |  |  | 1.4
|  | Lavatory |  |  |  | Private |  |  |  | Faucet |  |  |  | 0.5 |  |  |  | 0.5 |  |  |  | 0.7
|  | Lavatory |  |  |  | Public |  |  |  | Faucet |  |  |  | 1.5 |  |  |  | 1.5 |  |  |  | 2
|  | Service sink |  |  |  | Offices, etc. |  |  |  | Faucet |  |  |  | 2.25 |  |  |  | 2.25 |  |  |  | 3
|  | Shower head |  |  |  | Public |  |  |  | Mixing valve |  |  |  | 3 |  |  |  | 3 |  |  |  | 4
|  | Shower head |  |  |  | Private |  |  |  | Mixing valve |  |  |  | 1 |  |  |  | 1 |  |  |  | 1.4
|  | Urinal |  |  |  | Public |  |  |  | 1• flushometer valve |  |  |  | 10 |  |  |  | - |  |  |  | 10.0
|  | Urinal |  |  |  | Public |  |  |  | 3// flushometer valve |  |  |  | 5 |  |  |  | - |  |  |  | 5
|  | Urinal |  |  |  | Public |  |  |  | Flush tank |  |  |  | 3 |  |  |  | - |  |  |  | 3
|  | Washing machine (8 lb) |  |  |  | Private |  |  |  | Automatic |  |  |  | 1 |  |  |  | 1 |  |  |  | 1.4
O 2018 International Plumbing Code (IPC) I& (i APPENDIX E SIZING OF WATER PIPING SYSTEM | [9 empty] | Upgrade to Premium | [5 empty] | Fiftn Version: Nov 2021
V
Kitchen sink |  |  |  |  | Private |  |  |  | Faucet |  |  | 1 |  |  |  |  | 1 |  |  |  | 1.4
Kitchen sink |  |  |  |  | Hotel, restaurant |  |  |  | Faucet |  |  | 3 |  |  |  |  | 3 |  |  |  | 4
Laundry trays (1 to 3) |  |  |  |  | Private |  |  |  | Faucet |  |  | 1 |  |  |  |  | 1 |  |  |  | 1.4
Lavatory |  |  |  |  | Private |  |  |  | Faucet |  |  | 0.5 |  |  |  |  | 0.5 |  |  |  | 0.7
Lavatory |  |  |  |  | Public |  |  |  | Faucet |  |  | 1.5 |  |  |  |  | 1.5 |  |  |  | 2
Service sink |  |  |  |  | Offices, etc. |  |  |  | Faucet |  |  | 2.25 |  |  |  |  | 2.25 |  |  |  | 3
Shower head |  |  |  |  | Public |  |  |  | Mixing valve |  |  | 3 |  |  |  |  | 3 |  |  |  | 4
Shower head |  |  |  |  | Private |  |  |  | Mixing valve |  |  | 1 |  |  |  |  | 1 |  |  |  | 1.4
Urinal |  |  |  |  | Public |  |  |  | 1• flushometer valve |  |  | 10 |  |  |  |  | - |  |  |  | 100
Urinal |  |  |  |  | Public |  |  |  | 3// flushometer valve |  |  | 5 |  |  |  |  | - |  |  |  | 5
Urinal |  |  |  |  | Public |  |  |  | Flush tank |  |  | 3 |  |  |  |  | - |  |  |  | 3
Washing machine (8 lb) |  |  |  |  | Private |  |  |  | Automatic |  |  | 1 |  |  |  |  | 1 |  |  |  | 1.4
Washing machine (8 lb) |  |  |  |  | Public |  |  |  | Automatic |  |  | 2.25 |  |  |  |  | 2.25 |  |  |  | 3
Washing machine (15 lb) |  |  |  |  | Public |  |  |  | Automatic |  |  | 3 |  |  |  |  | 3 |  |  |  | 4
Water closet |  |  |  |  | Private |  |  |  | Flushometer valve |  |  | 6 |  |  |  |  | - |  |  |  | 6
Water closet |  |  |  |  | Private |  |  |  | Flush tank |  |  | 2.2 |  |  |  |  | - |  |  |  | 2.2
Water closet |  |  |  |  | Public |  |  |  | Flushometer valve |  |  | 10 |  |  |  |  | - |  |  |  | 10
Water closet |  |  |  |  | Public |  |  |  | Flush tank |  |  | 5 |  |  |  |  | - |  |  |  | 5
Water closet |  |  |  |  | Public or private |  |  |  | Flushometer tank |  |  | 2 |  |  |  |  | - |  |  |  | 2
q
For SI: 1 inch= 25.4 mm, 1 pound= 0.454 kg. a. For fiXlures not listed, loads should be assumed by comparing the fiXlure to one listed using water in similar quantities and at similar rates. The assigned loads for fiXlures wrth both hot and cold water supplies are given for separate hot and cold water loads and for total load. The separate hot and cold water loads being three-fourths of the total load for the fiXlure in each case.
? 2018 International Plumbing Code (IPC) m3 APPENDIX i: SIZING OF WATER ?IPING SYSTEM | [5 empty] | Upgrade to Premium |  | Fifth Vers1on: ov 2021
TABLE E103.3(3) TABLE FOR ESTIMATING DEMAND
| SUPPLY SYSTEMS PREDOMINANTLY FOR FLUSH TANKS | [11 empty] | SUPPLY SYSTEMS PREDOMINANTLY FOR FLUSHOMETERVALVES
| Load |  | Oemand | [9 empty] | Load | [5 empty] | Demand
| (Water supply fixture units) |  | (Gallons per minute) |  |  |  |  | (Cubic feet per minute) |  |  |  |  | (Water supply fixture units) | [5 empty] | (Gallons per minute) |  |  |  | (Cubic feet per minute)
| 1 |  | 3 |  |  |  |  | 0.04104 |  |  |  |  | - | [5 empty] | - |  |  |  | -
| 2 |  | 5 |  |  |  |  | 0.0684 |  |  |  |  | - | [5 empty] | - |  |  |  | -
| 3 |  | 6.5 |  |  |  |  | 0.86892 |  |  |  |  | - | [5 empty] | - |  |  |  | -
| 4 |  | 8 |  |  |  |  | 1.0694 |  |  |  |  | - | [5 empty] | - |  |  |  | -
| 5 |  | 9.4 |  |  |  |  | 1.2566 |  |  |  |  | 5 | [5 empty] | 15 |  |  |  | 2.0052
| 6 |  | 10.7 |  |  |  |  | 1.4304 |  |  |  |  | 6 | [5 empty] | 17.4 |  |  |  | 2.326
| 7 |  | 11.8 |  |  |  |  | 1.5TT424 |  |  |  |  | 7 | [5 empty] | 19.8 |  |  |  | 2.6464
| 8 |  | 12.8 |  |  |  |  | 1.7111 |  |  |  |  | 8 | [5 empty] | 22.2 |  |  |  | 2.9677
| 9 |  | 13.7 |  |  |  |  | 1.8314 |  |  |  |  | 9 | [5 empty] | 24.6 |  |  |  | 3.2885
| 10 |  | 14.6 |  |  |  |  | 1.9517 |  |  |  |  | 10 | [5 empty] | 27 |  |  |  | 3.6094
| 11 |  | 15.4 |  |  |  |  | 2.0587 |  |  |  |  | 11 | [5 empty] | 27.8 |  |  |  | 3.7163
| 12 |  | 16 |  |  |  |  | 2.1389 |  |  |  |  | 12 | [5 empty] | 28.6 |  |  |  | 3.8232
| 13 |  | 16.5 |  |  |  |  | 2.2057 |  |  |  |  | 13 | [5 empty] | 29.4 |  |  |  | 3.9302
| 14 |  | 17 |  |  |  |  | 2.2726 |  |  |  |  | 14 | [5 empty] | 30.2 |  |  |  | 4.0371
| 15 |  | 17.5 |  |  |  |  | 2.3394 |  |  |  |  | 15 | [5 empty] | 31 |  |  |  | 4.1441
| 16 |  | 18 |  |  |  |  | 2.9062 |  |  |  |  | 16 | [5 empty] | 31.8 |  |  |  | 4.241
| 17 |  | 18.4 |  |  |  |  | 2.4597 |  |  |  |  | 17 | [5 empty] | 32.6 |  |  |  | 4.358
| 18 |  | 18.8 |  |  |  |  | 2.5132 |  |  |  |  | 18 | [5 empty] | 33.4 |  |  |  | 4.4649
| 19 |  | 19.2 |  |  |  |  | 2.5667 |  |  |  |  | 19 | [5 empty] | 34.2 |  |  |  | 4.5719
| 20 |  | 19.6 |  |  |  |  | 2.6201 |  |  |  |  | 20 | [5 empty] | 35 |  |  |  | 4.6788
| 25 |  | 21.5 |  |  |  |  | 2.8741 |  |  |  |  | 25 | [5 empty] | 38 |  |  |  | 5.0798
| 30 |  | 23.3 |  |  |  |  | 3.1147 |  |  |  |  | 30 | [5 empty] | 42 |  |  |  | 5.6136
| 35 |  | 24.9 |  |  |  |  | 3.3286 |  |  |  |  | 35 | [5 empty] | 44 |  |  |  | 5.8819
| 40 |  | 26.3 |  |  |  |  | 3.5158 |  |  |  |  | 40 | [5 empty] | 46 |  |  |  | 6.1493
| 45 |  | 27.7 |  |  |  |  | 3.7029 |  |  |  |  | 45 | [5 empty] | 48 |  |  |  | 6.4166
| 50 |  | 29.1 |  |  |  |  | 3.8901 |  |  |  |  | 50 | [5 empty] | 50 |  |  |  | 6.684
| 60 |  | 32 |  |  |  |  | 4.2778 |  |  |  |  | 60 | [5 empty] | 54 |  |  |  | 7.2187
| 70 |  | 35 |  |  |  |  | 4.6788 |  |  |  |  | 70 | [5 empty] | 58 |  |  |  | 7.7534
Q 2018 International Plumbing Code (IPC) tm APPENDIX E SIZING OF WATER ?l?lNG SYSTEM | [5 empty] | Upgrade to Premium |  |  | fifth Version: ov 2021
| 30 |  |  | 23.3 |  |  |  |  | 3.1147 | [5 empty] | 30 |  |  |  |  | 42 |  |  |  | 5.6136
| 35 |  |  | 24.9 |  |  |  |  | 3.3286 | [5 empty] | 35 |  |  |  |  | 44 |  |  |  | 5.8819
| 40 |  |  | 26.3 |  |  |  |  | 3.5158 | [5 empty] | 40 |  |  |  |  | 46 |  |  |  | 6.1493
| 45 |  |  | 27.7 |  |  |  |  | 3.7029 | [5 empty] | 45 |  |  |  |  | 48 |  |  |  | 6.4166
| 50 |  |  | 29.1 |  |  |  |  | 3.8901 | [5 empty] | 50 |  |  |  |  | 50 |  |  |  | 6.684
| 60 |  |  | 32 |  |  |  |  | 4.2778 | [5 empty] | 60 |  |  |  |  | 54 |  |  |  | 7.2187
| 70 |  |  | 35 |  |  |  |  | 4.6788 | [5 empty] | 70 |  |  |  |  | 58 |  |  |  | 7.7534
| 80 |  |  | 38 |  |  |  |  | 5.0798 | [5 empty] | 80 |  |  |  |  | 61.2 |  |  |  | 8.1812
| 90 |  |  | 41 |  |  |  |  | 5.4809 | [5 empty] | 90 |  |  |  |  | 64.3 |  |  |  | 8.5956
| 100 |  |  | 43.5 |  |  |  |  | 5.8151 | [5 empty] | 100 |  |  |  |  | 67.5 |  |  |  | 9.0234
| 120 |  |  | 48 |  |  |  |  | 6.4166 | [5 empty] | 120 |  |  |  |  | 73 |  |  |  | 9.7586
| 140 |  |  | 52.5 |  |  |  |  | 7.0182 | [5 empty] | 140 |  |  |  |  | 77 |  |  |  | 10.2934
| 160 |  |  | 57 |  |  |  |  | 7.6198 | [5 empty] | 160 |  |  |  |  | 81 |  |  |  | 10.8281
| 180 |  |  | 61 |  |  |  |  | 8.1545 | [5 empty] | 180 |  |  |  |  | 85.5 |  |  |  | 11.4296
| 200 |  |  | 65 |  |  |  |  | 8.6892 | [5 empty] | 200 |  |  |  |  | 90 |  |  |  | 12.0312
| 225 |  |  | 70 |  |  |  |  | 9.3576 | [5 empty] | 225 |  |  |  |  | 95.5 |  |  |  | 12.7664
| 250 |  |  | 75 |  |  |  |  | 10.026 | [5 empty] | 250 |  |  |  |  | 101 |  |  |  | 13.5017
| 275 |  |  | 80 |  |  |  |  | 10.6944 | [5 empty] | 275 |  |  |  |  | 104.5 |  |  |  | 13.9696
| 300 |  |  | 85 |  |  |  |  | 11.3628 | [5 empty] | 300 |  |  |  |  | 108 |  |  |  | 14.4374
| 400 |  |  | 105 |  |  |  |  | 14.0364 | [5 empty] | 400 |  |  |  |  | 127 |  |  |  | 16.9774
| 500 |  |  | 124 |  |  |  |  | 16.5763 | [5 empty] | 500 |  |  |  |  | 143 |  |  |  | 19.1162
| 750 |  |  | 170 |  |  |  |  | 22.7256 | [5 empty] | 750 |  |  |  |  | 177 |  |  |  | 23.6614
| 1000 |  |  | 208 |  |  |  |  | 27.8054 | [5 empty] | 1000 |  |  |  |  | 208 |  |  |  | 27.8054
| 1250 |  |  | 239 |  |  |  |  | 31.9495 | [5 empty] | 1250 |  |  |  |  | 239 |  |  |  | 31.9495
| 1500 |  |  | 269 |  |  |  |  | 35.9599 | [5 empty] | 1500 |  |  |  |  | 269 |  |  |  | 35.9599
| 1750 |  |  | 297 |  |  |  |  | 39.703 | [5 empty] | 1750 |  |  |  |  | 297 |  |  |  | 39.703
| 2000 |  |  | 325 |  |  |  |  | 43.446 | [5 empty] | 2000 |  |  |  |  | 325 |  |  |  | 43.446
| 2500 |  |  | 380 |  |  |  |  | 50.7984 | [5 empty] | 2500 |  |  |  |  | 380 |  |  |  | 50.7984
| 3000 |  |  | 433 |  |  |  |  | 57.8834 | [5 empty] | 3000 |  |  |  |  | 433 |  |  |  | 57.8834
| 4000 |  |  | 525 |  |  |  |  | 70.182 | [5 empty] | 4000 |  |  |  |  | 525 |  |  |  | 70.182
| 5000 |  |  | 593 |  |  |  |  | 79.2722 | [5 empty] | 5000 |  |  |  |  | 593 |  |  |  | 79.27224 I
0
I

## Table for Estimating Demand
| Supply Systems for Flush Tanks |  |  |  |  | Supply Systems for Flush Valves
Load | Demand |  |  |  | Load | Demand
(wsfu) | (Gallons per minute) |  | (Cubic feet per minute) |  | (Wsfu) | (GPM) | (Cubic feet per minute)
1 |  | 3 |  | 0.04104 | - | - | -
2 |  | 5 |  | 0.0684 | - | - | -
3 |  | 6.5 |  | 0.86892 | - | - | -
4 |  | 8 |  | 1.0694 | - | - | -
5 |  | 9.4 |  | 1.2566 | 5 | 15 | 2.0052
6 |  | 10.7 |  | 1.4304 | 6 | 17.4 | 2.326
7 |  | 11.8 |  | 1.5TT424 | 7 | 19.8 | 2.6464
8 |  | 12.8 |  | 1.7111 | 8 | 22.2 | 2.9677
9 |  | 13.7 |  | 1.8314 | 9 | 24.6 | 3.2885
10 |  | 14.6 |  | 1.9517 | 10 | 27 | 3.6094
11 |  | 15.4 |  | 2.0587 | 11 | 27.8 | 3.7163
12 |  | 16 |  | 2.1389 | 12 | 28.6 | 3.8232
13 |  | 16.5 |  | 2.2057 | 13 | 29.4 | 3.9302
14 |  | 17 |  | 2.2726 | 14 | 30.2 | 4.0371
15 |  | 17.5 |  | 2.3394 | 15 | 31 | 4.1441
16 |  | 18 |  | 2.9062 | 16 | 31.8 | 4.241
17 |  | 18.4 |  | 2.4597 | 17 | 32.6 | 4.358
18 |  | 18.8 |  | 2.5132 | 18 | 33.4 | 4.4649
19 |  | 19.2 |  | 2.5667 | 19 | 34.2 | 4.5719
20 |  | 19.6 |  | 2.6201 | 20 | 35 | 4.6788
25 |  | 21.5 |  | 2.8741 | 25 | 38 | 5.0798
30 |  | 23.3 |  | 3.1147 | 30 | 42 | 5.6136
35 |  | 24.9 |  | 3.3286 | 35 | 44 | 5.8819
40 |  | 26.3 |  | 3.5158 | 40 | 46 | 6.1493
45 |  | 27.7 |  | 3.7029 | 45 | 48 | 6.4166
50 |  | 29.1 |  | 3.8901 | 50 | 50 | 6.684
60 |  | 32 |  | 4.2778 | 60 | 54 | 7.2187
70 |  | 35 |  | 4.6788 | 70 | 58 | 7.7534
80 |  | 38 |  | 5.0798 | 80 | 61.2 | 8.1812
90 |  | 41 |  | 5.4809 | 90 | 64.3 | 8.5956
100 |  | 43.5 |  | 5.8151 | 100 | 67.5 | 9.0234
120 |  | 48 |  | 6.4166 | 120 | 73 | 9.7586
140 |  | 52.5 |  | 7.0182 | 140 | 77 | 10.2934
160 |  | 57 |  | 7.6198 | 160 | 81 | 10.8281
180 |  | 61 |  | 8.1545 | 180 | 85.5 | 11.4296
200 |  | 65 |  | 8.6892 | 200 | 90 | 12.0312
225 |  | 70 |  | 9.3576 | 225 | 95.5 | 12.7664
250 |  | 75 |  | 10.026 | 250 | 101 | 13.5017
275 |  | 80 |  | 10.6944 | 275 | 104.5 | 13.9696
300 |  | 85 |  | 11.3628 | 300 | 108 | 14.4374
400 |  | 105 |  | 14.0364 | 400 | 127 | 16.9774
500 |  | 124 |  | 16.5763 | 500 | 143 | 19.1162
750 |  | 170 |  | 22.7256 | 750 | 177 | 23.6614
1000 |  | 208 |  | 27.8054 | 1000 | 208 | 27.8054
1250 |  | 239 |  | 31.9495 | 1250 | 239 | 31.9495
1500 |  | 269 |  | 35.9599 | 1500 | 269 | 35.9599
1750 |  | 297 |  | 39.703 | 1750 | 297 | 39.703
2000 |  | 325 |  | 43.446 | 2000 | 325 | 43.446
2500 |  | 380 |  | 50.7984 | 2500 | 380 | 50.7984
3000 |  | 433 |  | 57.8834 | 3000 | 433 | 57.8834
4000 |  | 525 |  | 70.182 | 4000 | 525 | 70.182
5000 |  | 593 |  | 79.2722 | 5000 | 593 | 79.2722

## load Values wsfu
FIXTURE | OCCUPANCY | TYPE OF SUPPLY CONTROL | LOAD VALUES(wsfu)
|  |  | Cold | Hot | Total
Bathroom group | Private | Flush tank | 2.7 | 1.5 | 3.6
Bathroom group | Private | Flushometer valve | 6 | 3 | 8
Bathtub | Private | Faucet | 1 | 1 | 1.4
Bathtub | Public | Faucet | 3 | 3 | 4
Bidet | Private | Faucet | 1.5 | 1.5 | 2
Combination fixture | Private | Faucet | 2.25 | 2.25 | 3
Dishwashing machine | Private | Automatic | - | 1.4 | 1.4
Drinking fountain | Offices, etc. | 3/8" valve | 0.25 | - | 0.25
Kitchen sink | Private | Faucet | 1 | 1 | 1.4
Kitchen sink | Hotel, restaurant | Faucet | 3 | 3 | 4
Laundry trays (1 to 3) | Private | Faucet | 1 | 1 | 1.4
Lavatory | Private | Faucet | 0.5 | 0.5 | 0.7
Lavatory | Public | Faucet | 1.5 | 1.5 | 2
Service sink | Offices, etc. | Faucet | 2.25 | 2.25 | 3
Shower head | Public | Mixing valve | 3 | 3 | 4
Shower head | Private | Mixing valve | 1 | 1 | 1.4
Urinal | Public | 1" flushometer valve | 10 | - | 10.0
Urinal | Public | 3/4" flushometer valve | 5 | - | 5
Urinal | Public | Flush tank | 3 | - | 3
Washing machine (8 lb) | Private | Automatic | 1 | 1 | 1.4
Kitchen sink | Private | Faucet | 1 | 1 | 1.4
Kitchen sink | Hotel, restaurant | Faucet | 3 | 3 | 4
Laundry trays (1 to 3) | Private | Faucet | 1 | 1 | 1.4
Lavatory | Private | Faucet | 0.5 | 0.5 | 0.7
Lavatory | Public | Faucet | 1.5 | 1.5 | 2
Service sink | Offices, etc. | Faucet | 2.25 | 2.25 | 3
Shower head | Public | Mixing valve | 3 | 3 | 4
Shower head | Private | Mixing valve | 1 | 1 | 1.4
Urinal | Public | 1" flushometer valve | 10 | - | 100
Urinal | Public | 3/4" flushometer valve | 5 | - | 5
Urinal | Public | Flush tank | 3 | - | 3
Washing machine (8 lb) | Private | Automatic | 1 | 1 | 1.4
Washing machine (8 lb) | Public | Automatic | 2.25 | 2.25 | 3
Washing machine (15 lb) | Public | Automatic | 3 | 3 | 4
Water closet | Private | Flushometer valve | 6 | - | 6
Water closet | Private | Flush tank | 2.2 | - | 2.2
Water closet | Public | Flushometer valve | 10 | - | 10
Water closet | Public | Flush tank | 5 | - | 5
Water closet | Public or private | Flushometer tank | 2 | - | 2